## Annex I TS - Prilog I TS
ANNEX I: TECHNICAL SPECIFICATION WITHIN PROCUREMENT NOTICE 5/2017
PRILOG I: TEHNIČKA SPECIFIKACIJA UZ OBAVIJEST O NABAVI 5/2017
Procurement subject: Thermo Oil Boiler Room
Predmet nabave: Vrelouljna kotlovnica
Summary: Subject of procurement is supply, delivery, installation, unloading, commissioning and warranty for quality of sold goods for Thermo Oil Boiler Room. Equipment includes 2 boilers of 2 x 3500 kW = 7000 kW in total. Purpose of the Thermo Oil Boiler Room is to heat thermal oil on the temperature up to 300°C and then heated thermo oil goes to the dryers on the lacquering and printing machines in order to achieve the required drying temperature of the lacquers. Thermal power of the boilers must be 2 x 3500 kW = 7000 kW in total. Outlet thermo oil temperature of boilers must be 300°C, and return/inlet temperature of thermo oil up to 260°C. Boilers will work on different type of fuels: LPG, LNG and alcohol. Thermo Oil Boiler Room will be build next to the RTO - Regenerative Thermal Oxidizer in order to use burning energy of RTO through Heat Exchanger (air - thermo oil) for heating the thermal oil for boiler room. The plant of Thermo Oil Boiler Room will be located outside the production plant (external location). Thermo Oil Boiler Room must be fully completed, workshop tested and documented, isolated and painted by supplier of the equipment.
Sažetak: Predmet nabave je kupnja, isporuka, instalacija, puštanje u pogon i usluga jamstva za ispravnost prodane robe za vrelouljnu kotlovnicu. Oprema obuhvaća 2 kotla od 2 x 3500 kW = 7000 kW sveukupno. Namjena vrelouljne kotlovnice je zagrijavanje termičkog ulja na temperature do 300°C kako bi se zagrijano ulje iskoristilo za grijanje sušionika na strojevima za lakiranje i tisak te postigla zahtijevana temperatura za sušenje lakova. Toplinska energija kotlova mora biti 2 x 3500 kW = 7000 kW sveukupno. Kotlovi moraju grijati ulje na temperature do 300°C, a povratna/ulazna temperatura ulja mora biti do 260°C. Kotlovi će raditi na različite tipove goriva: LPG, LNG i alkohol. Kotlovnica će se nalaziti uz RTO - Regenerativni termički oksidator kako bi se preko izmjenjivača topline (zrak - termoulje) iskoristila energija spaljivanja za zagrijavanje ulja u kotlovima. Postrojenje za kotlovnicu bit će smješteno vani, izvan proizvodnog pogona (vanjski smještaj). Kotlovnica mora biti kompletirana, radionički ispitana i dokumentirana, izolirana i obojana od strane dobavljača opreme.
Column 1-2 should be completed by the Contracting Authority. Column 3-4 should be completed by the Tenderer (Column 3 is to be filled in by the Tenderer and must detail what is offered, Column 4 allows the Tenderer to make comments on its proposed supply and to make eventual references to the documentation). Column 5 is reserved for the Evaluation Committee. The documentation supplied should clearly indicate (highlight, mark) the offered models and the eventual options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the Evaluation Committee. The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications. Unless otherwise specified, the requirements in these Technical Specifications are presented as a minimum standard which the offered goods must meet. Stupce 1-2 popunjava Naručitelj. Stupce 3-4 popunjava Ponuditelj (u stupcu 3 se navode tehnički podaci o ponuđenoj opremi, a u stupcu 4 Ponuditelj može navesti komentar). Stupac 5 popunjava Povjerenstvo za ocjenu ponuda. U dokumentaciji mora biti jasno naznačen (istaknut, označen) model ponuđene opreme, kao i eventualne opcije, ukoliko ih ima, tako da ocjenjivači mogu jasno utvrditi točnu konfiguraciju opreme. Ponuda mora biti jasna, s jasnim podacima o modelu i karakteristikama opreme kako bi ocjenjivači mogli objektivno ocijeniti pristiglu ponudu i usporediti ju s ostalim ponudama. Tehnička specifikacija koja nije jasna može biti odbačena. Ukoliko nije drugačije navedeno, zahtjevi navedeni u tehničkoj specifikaciji predstavljaju minimalne zahtjeve za traženu opremu.
1 – GENERAL REQUIREMENTS / OPĆI ZAHTJEVI 1.1 General requirements applying to all of the items / Opći zahtjevi primjenjivi na sve stavke
1. All technical requirements listed in the technical specifications are to be considered „or equal“./ Za sve tražene specifikacije/karakteristike koje su navedene u tehničkim specifikacijama vrijedi "ili jednakovrijedno“.
2. All equipments should be new, unused, not refurbished, most recent models and should have no any defects. The tenderers should not propose any equipment that is announced as end-of-line by the manufacturer./ Oprema mora biti nova, nekorištena, neobnovljena, najnoviji model i mora biti bez defekata. Dobavljači ne smiju predložiti opremu za koju je najavljen kraj linije proizvoda od strane proizvođača.
3. All required components that are not stated explicitly in this Technical Specifications document but are necessary for successful solution to the specifications herein shall be proposed./ Sve potrebne komponente koje nisu eksplicitno navedene u ovoj tehničkoj specifikaciji, a neophodne su za funkcionalno riješenje prema specifikacijama moraju biti predložene.
4. The tender price is determined as turn-key, with the exception of the cost calculation of Pipeline thermal oil in point 2.13. of Technical Specification which will be made according to the real situation after the completion. Tenderer must offer the price for Pipeline thermal oil in point 2.13. in Price Shedule according to the point 2.13. of Technical Specification./ Cijena ponude je određena po principu "ključ u ruke", uz iznimku obračuna Cjevovoda termičkog ulja u točki 2.13. Tehničke specifikacije koji će se izvršiti prema stvarnom stanju po završetku posla. Ponuditelj mora ponuditi cijenu Cjevovoda termičkog ulja u točki 2.13. Troškovnika sukladno točki 2.13. Tehničke specifikacije.
5. All software shall be full version licensed to “Aluflexpack novi", with no licence expiration limitations./ Sav software mora biti puna verzija licencirana na "Aluflexpack novi", bez vremenskog ograničenja isteka licence.
1.2 Training requirements / Zahtjevi za edukaciju
1. The Contractor shall perform the on-site trainings of users in start-up, set-up, operation and use of all the equipment supplied. Instruction and training in the use of the equipment must be provided and conducted at the time of installation. / Dobavljač će izvršiti obuku osoblja na lokaciji za upućivanje, podešavanje i korištenje sve isporučene opreme. Upute i obuka za upotrebu moraju biti dostupne i provedene u vrijeme instalacije opreme.
1 | 2 |  | 3 | 4 | 5
| Specifications Required/ Zahtjevane specifikacije |  | Specifications Offered/ Ponuđene specifikacije | Notes, remarks, ref to documentation/ Bilješke, napomene | Evaluation Committe’s notes (YES / NO)/ Ocjena povjerenstva (DA/NE)
1. | Thermo Oil Boiler Room / Vrelouljna kotlovnica / 1pcs/1kom
| Technical specification / Tehničke karakteristike | Two thermal oil boilers (2 pcs) of thermal power 2 x 3500 kW = 7000 kW in total, for outdoor use with a corresponding shut-off, measurement, safety and regulating valves and air heaters / Dva vrelouljna kotla (2 kom) toplinske snage 2 x 3500 kW = 7000 kW sveukupno, za vanjsku primjenu s pripadajućom zapornom, mjernom, sigurnosnom i regulacijskom armaturom i zagrijačem zraka
Operating temperature of the oil - output 300°C; return 260°C / Radna temperatura ulja ulaz 300°C; povrat 260°C
The fuel - liquified petroleum gas (LPG) or liquefied natural gas (LNG), alcohol (Etanol CH3CH2OH 95%) and 5% MEK (C2H8O) / Gorivo - ukapljeni i prirodni plin (LPG i LNG), alkohol (Etanol CH3CH2OH 95%) i 5% MEK (C2H8O)
Efficiency > more than 90% / Stupanj iskorištenja > više od 90%
Oil supply pressure 3,5 bar and pressure drop supply/discharge 1,5 bar / Zahtijevani izlazni tlak termo ulja 3,5 bar i maksimalni pad tlaka izlaz-ulaz 1,5 bar
The boilers are to be fully completed, workshop tested and documented, isolated and painted / Kotlovi moraju biti kompletirani, radionički ispitani i dokumentirani, izolirani i obojani
2. | Dodatna oprema / Additional equipment:
2.1. | Burners / Plamenici za loženje / 2 pcs/2 kom
| Technical specification / Tehničke karakteristike | Burners to burn propane-butane gas or natural gas or alcohol. / Plamenici za loženje propan-butan plinom ili zemnim plinom ili alkoholom.
2.2. | Control panel of the boiler room / Upravljački ormar kotlovnice / 1 pcs/1kom
| Technical specification / Tehničke karakteristike | The control panel of the boiler room for the control of devices in the boiler room/ Upravljački ormar kotlovnice za kontrolu rada uređaja u kotlovnici
2.3. | Control panel for the secondary circuit / Upravljački ormar za regulaciju sekundarnog kruga / 1pcs/1kom
| Technical specification / Tehničke karakteristike | Control panel for the secondary circuit/ Upravljački ormar za regulaciju sekundarnog kruga
2.4. | PLC for control of boiler room / PLC za kontrolu rada kotlovnice / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | PLC for control of boiler room / PLC za kontrolu rada kotlovnice
2.5. | Circulation centrifugal pumps for thermo oil / Cirkulacione centrifugalne pumpe za termičko ulje / 7pcs/7kom
| Technical specification / Tehničke karakteristike | Circulation centrifugal pumps for thermal oil necessary for the operation of the boiler room: the primary circuit - 3 pcs, the secondary circuit: machine 1- 1 pcs, machine 2 - 2 pcs, and secondary circuit climatization-heating - 1 pcs./ Cirkulacione centrifugalne pumpe za termičko ulje potrebne za funkcioniranje kotlovnice: za primarni krug -3 kom, za sekundarni krug: stroj 1 - 1 kom, stroj 2 - 2 kom, i za sekundarni krug klima-grijanje - 1 kom.
2.6. | Thermo oil separator / Razdjelnik termičkog ulja / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | Thermo oil separator/ Razdjelnik termičkog ulja
2.7. | Thermo oil tank / Sabirnik termičkog ulja / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | Thermal oil tank/ Sabirnik termičkog ulja
2.8. | Chimney for boiler room / Dimnjak za kotlovnicu / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | Chimney for boiler room: min height 14m/ Dimnjak za kotlovnicu: min visina 14m
2.9. | Closed expansion tank / Zatvorena ekspanziona posuda / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | Closed expansion tank for thermal oil V = 8 m3, the maximum temperature of 300°C/ Zatvorena ekspanziona posuda za termičko ulje V = 8 m3, za maksimalnu temperaturu od 300°C
2.10. | Venting buffer vessel / Odzračna tampon posuda / 1 pcs/1kom
| Technical specification / Tehničke karakteristike | Venting buffer vessel for the thermo oil V= 500 l / Odzračna tampon posuda za termičko ulje V =500 l
2.11. | Discharge vessel for the thermal oil/ Ispusna posuda za termičko ulje / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | Discharge collection vessel for thermal oil V = 15 m3, the maximum temperature of 300°C, discharge pressure of 2 bar / Ispusna sabirna posuda za termičko ulje V = 15 m3, za max temperaturu od 300°C, tlak ispuštanja 2 bar
2.12. | Pumping station for charging - discharging system / Pumpna stanica za punjenje – pražnjenje sistema / 1pcs/1kom
| Technical specification / Tehničke karakteristike | Pumping station for charging - discharging system thermal oil/ Pumpna stanica za punjenje - pražnjenje sistema termičkim uljem
2.13. | Pipeline thermal oil / Cjevovod termičkog ulja / 1 pcs/1 kom
| Technical specification / Tehničke karakteristike | Pipeline thermal oil, seamless steel pipes withouth isolation, weight cca 15.000 kg / Cjevovod termičkog ulja od čeličnih bešavnih cijevi bez izolacije u količini cca 15.000 kg
3. | Anticorosive protection / Antikorozivna zaštita / 1pcs/1kom
| Technical specification / Tehničke karakteristike | AC protection unisolated piping and equipment / AK zaštita neizoliranih cjevovoda i opreme
4. | Documentation / Dokumentacija / 1pcs/1kom
| Documentation / Dokumentacija | After the final Acceptance Test, all documentation will be delieverd in electonic (CD-Rom (DVD) and written form with documents in PDF or Excel or dwg format), and will be created in Croatian or English, and includes: / Nakon završetka i prihvaćanja rezultata testne proizvodnje, sva dokumentacija (CD (DVD) s dokumentima u PDF ili Excel ili dwg formatu) bit će izrađena na hrvatskom ili engleskom jeziku, i obuhvaća:
Executable engineering documentation / Izvedbena strojarska dokumentacija
Technical documentation (attest documentation and operating instructions) / Tehnička dokumentacija (atesna dokumentacija i pogonske upute)
Drawings (Layout drawings and functionality drawings) / Nacrti (Nacrti postrojenja i funkcionalna shema postrojenja)
5. | Installation and Commissioning/ Montaža i puštanje u rad / 1 lump sum/ 1 paušal
All the equipments shall be provided, installed, put into operation and tested completely to ensure that the unit is capable of operating to the required technical and quality specifications. / Sva oprema biti će isporučena, instalirana, puštena u rad i kompletno isprobana da bi se osiguralo da funkcioniranje u potpunosti zadovoljava sve tehničke specifikacije i zahtjeve kvalitete.